section 22 05 29

# HANGERS AND SUPPORTS FOR PLUMBING PIPING AND EQUIPMENT

PART – GENERAL

  - SUMMARY

- Section Includes pipe and equipment supports and hangers

  - REFERENCES

- ASME B31.1 (American Society of Mechanical Engineers) – Power Piping.

- MSS SP58 (Manufacturers Standardization Society of the Valve and Fittings Industry) – Pipe Hangers and Supports – Materials, Design and Manufacturer.

- NFPA 13 2010 (National Fire Protection Association) – Installation of Sprinkler Systems.

- UPC 2012 (Uniform Plumbing Code) – Defines support spacing of hangers

1.03		SUBMITTALS

- Section 01 33 00 – Submittal Procedures: Submittal sheets with technical data available.

- Product Data: Submit manufacturers catalog data including load capacity.

- Design Data: Indicate load carrying capacity of trapeze, multiple pipe, and riser support hangers.

1.04	QUALITY ASSURANCE

- Hangers and supports shall have the manufacturer’s name and applicable size stamped in the part itself for identification.

- Hangers and supports shall be designed and manufactured in accordance with MSS SP 58.

- Hangers and supports for sprinkler piping shall conform to NFPA 13 specification.

PART 2 – PRODUCTS

2.01	MANUFACTURERS

- Manufacturer: Pipe hangers and supports shall be manufactured by Hilti, Inc.

2.02	MANUFACTURED UNITS

- Pipe Hangers and Supports for Steel Pipe: The following is a list of acceptable hangers and supports for steel pipe with or without insulation:

- Speed Lock Clevis (SLC) hanger: Hilti SLC-EG 2” - 8”

- Insulation Shield: Hilti Speed Lock (SLIS) Insulation Shield MH-SLIS  2” – 8”

- Standard Clevis hanger: Hilti SDC-EG ½” - 14”

- Short Hinged Riser Clamps (uninsulated pipe only:)  Hilti Speed Lock Riser MH-SLR-S 1” – 4”

- Long Hinged Riser Clamps:  Hilti Speed Lock Riser MH-SLR-LH 1” – 4”

- Slotted Riser Clamps:  Hilti Speed Lock Riser  MH-SLR-LS     3” – 10”

- Malleable Iron Split Ring hanger: Hilti SR-EG ½” - 4”

- Adjustable Swivel / Loop hanger: Hilti LH ½” - 8”

- Beam Clamps: Hilti BC ¼” - ¾”

- Continuous Concrete Insert Strut – Hilti Strut CIS 138-12 & Strut CIS 1316-12

- Steel Concrete Spot Insert – Hilti Concrete Insert EG & Plain

- Pipe Hangers and Supports for Copper Pipe / Tube:  The following is a list of acceptable hangers and supports for copper pipe / tube without insulation:

1.   	Hilti Copper Speed Lock Riser Clamp MH-CSLR-LH 1” – 4”

2.   	Malleable Iron Copper Split ring hanger – Hilti Copper SR ½” - 3”

- Trapeze Supports

- Trapeze Supports shall be constructed using 12 gauge structural steel conforming to ASTM A1011 GR. 33 and have a minimum dimension of 1 5/8” wide by 1 5/8” deep.  Hilti strut HS-158-12 or stronger shall be used as the primary supporting member.

- Piping shall be restrained on the strut using strut clamps.  The following Strut Clamps shall be used:

Rigid Pipe: Hilti Rigid Strut Clamps R45 ½” – 8” or Hilti RBA  ½” - 6”

Copper Pipe – Hilti MH-CB 3/8” – 4”

2.03	ACCESSORIES

- Hanger Rods: Mild steel threaded both ends, continuous threaded.

- Split Nut:  Hilti MH-SLT Split Nut and Washer may be installed at any position on the continuous threaded rod.

2.04	HANGER SPACING

- All piping shall be supported properly to avoid any sagging.  Hanger spacing shall be determined using either Chapter 2, Part 5, Section 121 (ASME B31.1 – Standard for Pressure and Power Piping) or UPC 2012 whichever is deemed applicable by the project engineer.

2.05	FINISHES

- Indoor Applications

- Hangers and supports for steel pipe shall be electro-galvanized or plain.

- Hangers and supports for copper pipe / tube shall have a copper electroplate finish.

- For Trapeze applications, strut shall have either a pre-galvanized finish conforming to ASTM A653 GR 33 specification or (for copper pipe and tubing) a green electro-deposition coating.

PART 3 – EXECUTION

  - INSTALLATION

- All Pipe Hanger and Support Installation shall conform to MSS-SP 58.  Installation of hangers, supports, clamps and attachments shall be performed to properly support piping from building structure.

  - PIPE HANGERS AND SUPPORTS

- Support horizontal piping as scheduled.

- Install hangers to provide minimum ½ inch (13 mm) space between finished covering and adjacent work.

### Place hangers within 12 inches (300 mm) of each horizontal elbow.

- Use hangers with 1½ inch (38 mm) minimum vertical adjustment.

- Support horizontal cast iron pipe adjacent to each hub, with 5 feet (1.5 m) maximum spacing between hangers.

- Support vertical piping independently of connected horizontal piping.

- Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

- Support riser piping independently of connected horizontal piping.

- Design hangers for pipe movement with disengagement of supported pipe.

### Prime coat exposed steel hangers and supports.  Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed.

###### SUPPORT SPACING

- All horizontal steel piping shall be supported in accordance with MSS-SP 58 tables 4.

###### END OF SECTION